## Feuil1
PLC Resource: INPUT
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory | Name | Description | Register | address | position
%IX0.0 | sensor_daylight | DAYLIGHT | BOOL | x
%IX0.1 | sensor_rain | RAIN | BOOL | x
%IX0.2 | sensor_breaker1 | BREAKERS | BOOL | x
%IX0.3 | sensor_breaker2 | BREAKERS | BOOL | x
%IX0.4 | sensor_breaker3 | BREAKERS | BOOL | x
%IX0.5 | sensor_UPS1 | BREAKERS | BOOL | x
%IX0.6 | sensor_UPS2 | BREAKERS | BOOL | x
%IX1.0 | so | MONITORING | BOOL | x
%IX1.1 | sc | MONITORING | BOOL | x
%IX1.2 | auto | MONITORING | BOOL | x
%IX1.3 | man | MONITORING | BOOL | x
%IX1.4 | rol1 | MONITORING | BOOL | x
%IX1.5 | rol2 | MONITORING | BOOL | x
%IX1.6 | rcl1 | MONITORING | BOOL | x
%IX1.7 | rcl2 | MONITORING | BOOL | x
%IX2.0 | mr | MONITORING | BOOL | x
%IX2.1 | nmr | MONITORING | BOOL | x
%IX2.2 | srs | MONITORING | BOOL | x
%IX4.0 | sensor_closed_1A | POSITION_ROOF_1 | BOOL | x
%IX4.1 | sensor_closed_1B | POSITION_ROOF_1 | BOOL | x
%IX4.2 | sensor_open_1A | POSITION_ROOF_1 | BOOL | x
%IX4.3 | sensor_open_1B | POSITION_ROOF_1 | BOOL | x
%IX4.4 | sensor_closed_2A | POSITION_ROOF_1 | BOOL | x
%IX4.5 | sensor_closed_2B | POSITION_ROOF_1 | BOOL | x
%IX4.6 | sensor_open_2A | POSITION_ROOF_1 | BOOL | x
%IX4.7 | sensor_open_2B | POSITION_ROOF_1 | BOOL | x
%IX5.0 | sensor_closed_1A_err | POSITION_ROOF_2 | BOOL | x
%IX5.1 | sensor_closed_1B_err | POSITION_ROOF_2 | BOOL | x
%IX5.2 | sensor_open_1A_err | POSITION_ROOF_2 | BOOL | x
%IX5.3 | sensor_open_1B_err | POSITION_ROOF_2 | BOOL | x
%IX5.4 | sensor_closed_2B_err | POSITION_ROOF_2 | BOOL | x
%IX5.5 | sensor_closed_2A_err | POSITION_ROOF_2 | BOOL | x
%IX5.6 | sensor_open_2A_err | POSITION_ROOF_2 | BOOL | x
%IX5.7 | sensor_open_2B_err | POSITION_ROOF_2 | BOOL | x
%IW6 | MDust_Value | M_DUST | UINT | x
%IW8 | d12v |  | UINT | x
PLC Resource: OUTPUT
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory | Name | Description | Register | address | position
%QX0.0 | Qclosing | Global_Variables | BOOL
%QX0.1 | Qopening | Global_Variables | BOOL
%QX1.0 | Qrelay_rain_1 | ReadWriteRegisters | BOOL
%QX1.1 | Qrelay_rain_2 | ReadWriteRegisters | BOOL
%QX2.0 | Qalarm_out | POSITION_FAILURE | x
Resource: SoftwareVersioning
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory | Name | Description | Register | address | position
%MB16 | Major | Soft versioning | USINT | x | 0x3008 | SoftwareVersioning1 |  | RO | 16392 | x
%MB17 | Minor | Soft versioning | USINT | x | 0x3008 | SoftwareVersioning1 |  | RO | 16392 | x
%MB18 | Development_stage | Soft versioning | USINT | x | 0x3009 | SoftwareVersioning2 |  | RO | 16393 | x
%MB19 | Revision_control | Soft versioning | USINT | x | 0x3009 | SoftwareVersioning2 |  | RO | 16393 | x
ReadWriteRegister
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory | Name | Description | Register | address | position
Alarms
%MX14.0 | alarm_close | POSITION_FAILURE | BOOL | x | 0x3007 | AL | alarm | RO | 16391 | 0
%MX14.1 | error_1 | POSITION_FAILURE | BOOL | x | 0x3007 | ER1 | error side 1 | RO | 16391 | 1
%MX14.2 | error_2 | POSITION_FAILURE | BOOL | x | 0x3007 | ER2 | error side 2 | RO | 16391 | 2
%MX14.3 | blocked_1 | POSITION_FAILURE | BOOL | x | 0x3007 | BL1 | blocked side 1 | RO | 16391 | 3
%MX14.4 | blocked_2 | POSITION_FAILURE | BOOL | x | 0x3007 | BL2 | blocked side 2 | RO | 16391 | 4
%MX14.5 | alarm_weather | CONTROL_WEATHER_STATION | BOOL | x | 0x3007 | ALW | alarm weather | RO | 16391 | 5
%MX14.6 | pos_reached_1 |  |  |  | 0x3007 | PR1 | position reached 1 | RO | 16391 | 6
%MX14.7 | pos_reached_2 |  |  |  | 0x3007 | PR2 | position reached 2 | RO | 16391 | 7
%MX15.0 | pos_reached |  |  |  | 0x3007 | PR | position reached | RO | 16391 | 8
%MX15.1
Commands
%MB1024 | CMD | ReadWriteRegisters | BYTE | x | 0x3200 | NONE (value="0") |  | RW | 16896 | x
%MB1024 | CMD | ReadWriteRegisters | BYTE | x | 0x3200 | CLOSE (value="1") |  | RW | 16896 | x
%MB1024 | CMD | ReadWriteRegisters | BYTE | x | 0x3200 | OPEN (value="2") |  | RW | 16896 | x
%MB1024 | CMD | ReadWriteRegisters | BYTE | x | 0x3200 | HIGH_OPEN (value="3") |  | RW | 16896 | x
EnableSensors1
[5 empty] | 0x3201 | ENABLE_ALL (value="65535") |  | RW | 16897 | x
[5 empty] | 0x3201 | DISABLE_ALL (value="0") |  | RW | 16897 | x
%MX1026.0 | EN_DAYLIGHT | ReadWriteRegisters | BOOL | x | 0x3201 | EnDL | enable daylight | RW | 16897 | 0
%MX1026.1 | EN_MDUST_SENSOR | ReadWriteRegisters | BOOL | x | 0x3201 | EnDU | enable M-dust sensor | RW | 16897 | 1
%MX1026.2 | EN_RAIN | ReadWriteRegisters | BOOL | x | 0x3201 | EnRN | enable rain | RW | 16897 | 2
%MX1026.3 | EN_SIDE1_isOPEN_A | ReadWriteRegisters | BOOL | x | 0x3201 | En1OA | enable side 1 open A | RW | 16897 | 3
%MX1026.4 | EN_SIDE1_isOPEN_B | ReadWriteRegisters | BOOL | x | 0x3201 | En1OB | enable side 1 open B | RW | 16897 | 4
%MX1026.5 | EN_SIDE1_isCLOSED_A | ReadWriteRegisters | BOOL | x | 0x3201 | EN1CA | enable side 1 closed A | RW | 16897 | 5
%MX1026.6 | EN_SIDE1_isCLOSED_B | ReadWriteRegisters | BOOL | x | 0x3201 | EN1CB | enable side 1 closed B | RW | 16897 | 6
%MX1026.7 | EN_SIDE2_isOPEN_A | ReadWriteRegisters | BOOL | x | 0x3201 | En2OA | enable side 2 open A | RW | 16897 | 7
%MX1027.0 | EN_SIDE2_isOPEN_B | ReadWriteRegisters | BOOL | x | 0x3201 | En2OB | enable side 2 open B | RW | 16897 | 8
%MX1027.1 | EN_SIDE2_isCLOSED_A | ReadWriteRegisters | BOOL | x | 0x3201 | EN2CA | enable side 2 closed A | RW | 16897 | 9
%MX1027.2 | EN_SIDE2_isCLOSED_B | ReadWriteRegisters | BOOL | x | 0x3201 | EN2CB | enable side 2 closed B | RW | 16897 | 10
%MX1027.3 | EN_CTR | ReadWriteRegisters | BOOL | x | 0x3201 | EnCTR | enable control | RW | 16897 | 11
%MX1027.4 | EN_DYLOS_DUST_SENSOR | ReadWriteRegisters | BOOL | x | 0x3201 | EnDU2 | enable Dylos dust sensor | RW | 16897 | 12
%MX1027.5 | EN_CONTROL_WEATHER_STATION | ReadWriteRegisters | BOOL | x | 0x3201 | EnWS | enable Weather station | RW | 16897 | 13
%MW1028 | MDust_ValMax | ReadWriteRegisters | UINT | x | 0x3202 | WriteDustUpperBound |  | RW | 16898 | x
%MW1030 | MDust_ValMin | ReadWriteRegisters | UINT | x | 0x3203 | WriteDustLowerBound |  | RW | 16899 | x
%MW1032 | CTR | ReadWriteRegisters | UINT | x | 0x3204 | Control |  | RW | 16900 | x
%MW1034 | CT | ReadWriteRegisters | UINT | x | 0x3205 | ControlTime |  | RW | 16901 | x
%MW1036 | OCT | ReadWriteRegisters | UINT | x | 0x3206 | OpeningClosingTime |  | RW | 16902 | x
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory | Name | Description | Register | address | position
DASFlags
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GO_ALL (value="65535") |  | RW | 16904 | x
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | DONT_GO_ALL (value="0") |  | RW | 16904 | x
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GO1 | go flag for DAS 1 | RW | 16904 | 0
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GO2 | go flag for DAS 2 | RW | 16904 | 1
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GO3 | go flag for DAS 3 | RW | 16904 | 2
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GO4 | go flag for DAS 4 | RW | 16904 | 3
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GO5 | go flag for DAS 5 | RW | 16904 | 4
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GO6 | go flag for DAS 6 | RW | 16904 | 5
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GO7 | go flag for DAS 7 | RW | 16904 | 6
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GO8 | go flag for DAS 8 | RW | 16904 | 7
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GO9 | go flag for DAS 9 | RW | 16904 | 8
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GO10 | go flag for DAS 10 | RW | 16904 | 9
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GO11 | go flag for DAS 11 | RW | 16904 | 10
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GO12 | go flag for DAS 12 | RW | 16904 | 11
%MW1040 | DAS_FLAGS | ReadWriteRegisters | WORD | x | 0x3208 | GGO | global go flag | RW | 16904 | 12
EnableSensors2
[5 empty] | 0x320A | ENABLE_ALL (value="65535") |  | RW | 16906 | x
[5 empty] | 0x320A | DISABLE_ALL (value="0") |  | RW | 16906 | x
%MX1044.0 | EN_sensor_breaker1 | ReadWriteRegisters | BOOL |  | 0x320A | EnB1 | Enable breaker 1 | RW | 16906 | 0
%MX1044.1 | EN_sensor_breaker2 | ReadWriteRegisters | BOOL |  | 0x320A | EnB2 | Enable breaker 2 | RW | 16906 | 1
%MX1044.2 | EN_sensor_breaker3 | ReadWriteRegisters | BOOL |  | 0x320A | EnB3 | Enable breaker 3 | RW | 16906 | 2
%MX1044.3 | EN_sensor_UPS1 | ReadWriteRegisters | BOOL |  | 0x320A | EnU1 | Enable UPS 1 | RW | 16906 | 3
%MX1044.4 | EN_sensor_UPS2 | ReadWriteRegisters | BOOL |  | 0x320A | EnU2 | Enable UPS 2 | RW | 16906 | 4
%MW1060 | Dylos_Big_ValMax | ReadWriteRegisters | UINT | 4000 | 0x3212 | DylosBigValMax |  | RW | 16914 | x
%MW1062 | Dylos_Small_ValMax | ReadWriteRegisters | UINT | 2000 | 0x3213 | DylosSmallValMax |  | RW | 16915 | x
DustPriority
%MB1070 | DustPriority | ReadWriteRegisters | BYTE | 4 | 0x3217 | M_DUST (value="0") |  | RW | 16919 | x
%MB1070 | DustPriority | ReadWriteRegisters | BYTE | 4 | 0x3217 | DYLOS (value="1") |  | RW | 16919 | x
%MB1070 | DustPriority | ReadWriteRegisters | BYTE | 4 | 0x3217 | DYLOS_BIG_DUST (value="2") |  | RW | 16919 | x
%MB1070 | DustPriority | ReadWriteRegisters | BYTE | 4 | 0x3217 | DYLOS_SMALL_DUST (value="3") |  | RW | 16919 | x
%MB1070 | DustPriority | ReadWriteRegisters | BYTE | 4 | 0x3217 | MDUST_AND_DYLOS (value="4") |  | RW | 16919 | x
%MB1092 | TOpen | ReadWriteRegisters | INT | 4000 | 0x3222 | OpeningTemporisation |  | RW | 16930 | x
%MB1094 | TClose | ReadWriteRegisters | INT | 4000 | 0x3223 | ClosingTemporisation |  | RW | 16931 | x
MEM_Variables
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory | Name | Description | Register | address | position
RoofPosition
%MX0.0 | isOpen_1_mem | MEM_Variables | BOOL | x | 0x3000 | O1 | is open side 1 | RO | 16384 | 0
%MX0.1 | isClosed_1_mem | MEM_Variables | BOOL | x | 0x3000 | C1 | is closed side 1 | RO | 16384 | 1
%MX0.2 | error_1_mem | MEM_Variables | BOOL | x | 0x3000 | E1 | error side 1 | RO | 16384 | 2
%MX0.3 | isOpen_2_mem | MEM_Variables | BOOL | x | 0x3000 | O2 | is open side 2 | RO | 16384 | 3
%MX0.4 | isClosed_2_mem | MEM_Variables | BOOL | x | 0x3000 | C2 | is closed side 2 | RO | 16384 | 4
%MX0.5 | error_2_mem | MEM_Variables | BOOL | x | 0x3000 | E2 | error side 2 | RO | 16384 | 5
SensorsRoofPosition
%MX2.0 | sensor_closed_1A_mem | MEM_Variables | BOOL | x | 0x3001 | SC1A | status closed side 1 A | RO | 16385 | 0
%MX2.1 | sensor_closed_1B_mem | MEM_Variables | BOOL | x | 0x3001 | SC1B | status closed side 1 B | RO | 16385 | 1
%MX2.2 | sensor_open_1A_mem | MEM_Variables | BOOL | x | 0x3001 | SO1A | status open side 1 A | RO | 16385 | 2
%MX2.3 | sensor_open_1B_mem | MEM_Variables | BOOL | x | 0x3001 | SO1B | status open side 1 B | RO | 16385 | 3
%MX2.4 | sensor_closed_2A_mem | MEM_Variables | BOOL | x | 0x3001 | SC2A | status closed side 2 A | RO | 16385 | 4
%MX2.5 | sensor_closed_2B_mem | MEM_Variables | BOOL | x | 0x3001 | SC2B | status closed side 2 B | RO | 16385 | 5
%MX2.6 | sensor_open_2A_mem | MEM_Variables | BOOL | x | 0x3001 | SO2A | status open side 2 A | RO | 16385 | 6
%MX2.7 | sensor_open_2B_mem | MEM_Variables | BOOL | x | 0x3001 | SO2B | status open side 2 B | RO | 16385 | 7
%MX3.0 | sensor_closed_1A_err_mem | MEM_Variables | BOOL | x | 0x3001 | EC1A | error closed side 1 A | RO | 16385 | 8
%MX3.1 | sensor_closed_1B_err_mem | MEM_Variables | BOOL | x | 0x3001 | EC1B | error closed side 1 B | RO | 16385 | 9
%MX3.2 | sensor_open_1A_err_mem | MEM_Variables | BOOL | x | 0x3001 | EO1A | error open side 1 A | RO | 16385 | 10
%MX3.3 | sensor_open_1B_err_mem | MEM_Variables | BOOL | x | 0x3001 | EO1B | error open side 1 B | RO | 16385 | 11
%MX3.4 | sensor_closed_2A_err_mem | MEM_Variables | BOOL | x | 0x3001 | EC2A | error closed side 2 A | RO | 16385 | 12
%MX3.5 | sensor_closed_2B_err_mem | MEM_Variables | BOOL | x | 0x3001 | EC2B | error closed side 2 B | RO | 16385 | 13
%MX3.6 | sensor_open_2A_err_mem | MEM_Variables | BOOL | x | 0x3001 | EO2A | error open side 2 A | RO | 16385 | 14
%MX3.7 | sensor_open_2B_err_mem | MEM_Variables | BOOL | x | 0x3001 | EO2B | error open side 2 B | RO | 16385 | 15
SensorStatus
%MX4.0 | Mdust_Dusty_mem | MEM_Variables | BOOL |  | 0x3002 | DUS1 | Mdust status 1 | RO | 12290 | 0
%MX4.1 | sensor_rain_mem | MEM_Variables | BOOL |  | 0x3002 | RNV | rain value | RO | 12290 | 1
%MX4.2 | sensor_daylight_mem | MEM_Variables | BOOL | x | 0x3002 | DLS | daylight status | RO | 12290 | 2
%MX4.3 |  |  |  |  | 0x3002 |  |  | RO | 12290 | 3
%MX4.4 |  |  |  |  | 0x3002 |  |  | RO | 12290 | 4
%MX4.5 |  |  |  |  | 0x3002 |  |  | RO | 12290 | 5
%MX4.6 |  |  |  |  | 0x3002 |  |  | RO | 12290 | 6
%MW6 | Mean_MDust_Value_mem | DUST | UINT | x | 0x3003 | mean DustValue |  | RO | 16387
%MW8 | MDust_Value_mem |  | UINT | x | 0x3004 | MDustValuemem |  | RO | 16388
%MX10.0 | Sensors_Detecting_mem | MEM_Variables | UINT | x | 0x3005 | SensorsDetecting |  | RO | 16389
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory | Name | Description | Register | address | position
CmdRemoteCtrBreakers
%MX12.0 | OPEN_MEM | Commands | BOOL | x | 0x3006 | O | opening! | RO | 16390 | 0
%MX12.1 | CLOSE_MEM | Commands | BOOL | x | 0x3006 | C | closing! | RO | 16390 | 1
%MX12.2 | CMD_HAND | Commands | BOOL | x | 0x3006 | HAND | CMD_HAND | RO | 16390 | 2
%MX12.6 | sensor_breaker1_mem | MEM_Variables | BOOL | x | 0x3006 | B1 | breaker 1 | RO | 16390 | 6
%MX12.7 | sensor_breaker2_mem | MEM_Variables | BOOL | x | 0x3006 | B2 | breaker 2 | RO | 16390 | 7
%MX13.0 | sensor_breaker3_mem | MEM_Variables | BOOL | x | 0x3006 | B3 | breaker 3 | RO | 16390 | 8
%MX13.1 | sensor_UPS1_mem | MEM_Variables | BOOL | x | 0x3006 | UPS1 | UPS1 4 | RO | 16390 | 9
%MX13.2 | sensor_UPS2_mem | MEM_Variables | BOOL | x | 0x3006 | UPS2 | UPS2 5 | RO | 16390 | 10
Monitoring
%MX20.0 | so_mem | MONITORING | BOOL |  | 0x300A | SO | STOP Open | RO | 16394 | 0
%MX20.1 | sc_mem | MONITORING | BOOL |  | 0x300A | SC | STOP Close | RO | 16394 | 1
%MX20.2 | auto_mem | MONITORING | BOOL |  | 0x300A | AUTO | Switch AUTO | RO | 16394 | 2
%MX20.3 | man_mem | MONITORING | BOOL |  | 0x300A | MAN | Switch MANUAL | RO | 16394 | 3
%MX20.4 | rol1_mem | MONITORING | BOOL |  | 0x300A | ROL1 | Roof Open Lamp 1 | RO | 16394 | 4
%MX20.5 | rol2_mem | MONITORING | BOOL |  | 0x300A | ROL2 | Roof Open Lamp 2 | RO | 16394 | 5
%MX20.6 | rcl1_mem | MONITORING | BOOL |  | 0x300A | RCL1 | Roof Close Lamp 1 | RO | 16394 | 6
%MX20.7 | rcl2_mem | MONITORING | BOOL |  | 0x300A | RCL2 | Roof Close Lamp 2 | RO | 16394 | 7
%MX21.0 | mr_mem | MONITORING | BOOL |  | 0x300A | MR | MR: Main Motor | RO | 16394 | 8
%MX21.1 | nmr_mem | MONITORING | BOOL |  | 0x300A | nMR | not MR: DC Motor Backup | RO | 16394 | 9
%MX21.2 | srs_mem | MONITORING | BOOL |  | 0x300A | SRS | Safety Relay STOP | RO | 16394 | 10
%MW22 | d12v_mem | MONITORING | UINT |  | 0x300B | Dust12VDC |  | RO | 16395 | x
ResetRelay
[5 empty] | 0x3207 | NONE (value="0") |  |  | 16903 | x
[5 empty] | 0x3207 | RESET_RELAY_1 (value="1") |  |  | 16903 | x
%MX1038.0 | Qrelay_rain_1_mem | ReadWriteRegisters | BOOL |  | 0x3207 | RESET_RELAY_2 (value="2") |  |  | 16903 | x
%MX1038.1 | Qrelay_rain_2_mem | ReadWriteRegisters | BOOL |  | 0x3207 | RESET_BOTH (value="3") |  |  | 16903 | x
[5 empty] | 0x3207 | R1 | Reset bit for relay 1 | RW | 16903 | 0
[5 empty] | 0x3207 | R2 | Reset bit for relay 2 | RW | 16903 | 1
%MW1050 | Old_HeartBeat_Weather_mem | ReadWriteRegisters | WORD | x | 0x320D | HeartBeatR |  | RW | 16909 | x
%MW1052 | HeartBeat_Weather_mem | ReadWriteRegisters | WORD | x | 0x320E | HeartBeatW |  | RW | 16910 | x
HeartBeatControl
%MX1054.0 | Alarm_Weather_mem | ReadWriteRegisters | BOOL | x | 0x320F | relay the weather control alarm |  | RW | 16911 | 0
%MW1064 | DylosBigParticles_mem | ReadWriteRegisters | WORD | x | 0x3214 | DylosBigValue |  | RW | 16916 | x
%MW1066 | DylosSmallParticles_mem | ReadWriteRegisters | WORD | x | 0x3215 | DylosSmallValue |  | RW | 16917 | x
%MB1072.0 | Dylos_Dusty_mem | ReadWriteRegisters | BOOL | x | 0x3218 | DylosDusty |  | RW | 16920 | x
%MX1080.0 | reset_mem |  |  |  | 0x321C
SIMULATION
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory | Name | Description | Register | address | position
%MX1200.0 | SIMULATION | SIM_Variables | BOOL | FALSE | 0x3258 | SIMULATION |  | RW | 16984 | 0
%MX1202.0 | is_ocs_connected_SIM | SIM_Variables | BOOL | TRUE | 0x3259 | is_ocs_connected_SIM |  | RW | 16985 | 0
%MX1210.0 | MDust_Dusty_SIM | SIM_Variables | BOOL | FALSE | 0x325D | MDustValue_SIM |  | RW | 16989 | 0
%MX1212.0 | Dylos_Dusty_SIM | SIM_Variables | BOOL |  | 0x325E | DylosDusty_SIM |  | RW | 16990 | 0
%MW1214 |  |  |  |  | 0x325F |  |  | RW | 16991
SIM_sensor_state
%MX1216.0 | sensor_daylight_SIM | SIM_Variables | BOOL | TRUE | 0x3260 | SimDS | SIM state daylight sensor | RW | 16992 | 0
%MX1216.1 | sensor_rain_SIM | SIM_Variables | BOOL | x | 0x3260 | SimRS | SIM state rain sensor | RW | 16992 | 1
%MX1216.2 | sensor_breaker1_SIM | SIM_Variables | BOOL | x | 0x3260 | SimB1 | SIM breaker1 state | RW | 16992 | 2
%MX1216.3 | sensor_breaker2_SIM | SIM_Variables | BOOL | x | 0x3260 | SimB2 | SIM breaker2 state | RW | 16992 | 3
%MX1216.4 | sensor_breaker3_SIM | SIM_Variables | BOOL | x | 0x3260 | SimB3 | SIM breaker3 state | RW | 16992 | 4
%MX1216.5 | sensor_UPS1_SIM | SIM_Variables | BOOL | x | 0x3260 | SimU1 | SIM UPS1 state | RW | 16992 | 5
%MX1216.6 | sensor_UPS2_SIM | SIM_Variables | BOOL | x | 0x3260 | SimU2 | SIM UPS2 state | RW | 16992 | 6
%MX1216.7 | Qrelay_rain_1_SIM | SIM_Variables | BOOL | x | 0x3260 | SimRR1 | SIM Rain1 | RW | 16992 | 7
%MX1217.0 | Qrelay_rain_2_SIM | SIM_Variables | BOOL | x | 0x3260 | SIMRR2 | SIM Rain2 | RW | 16992 | 8
SIM_Roof_State
%MX1218.0 | Qclosing_SIM | SIM_Variables | BOOL | FALSE | 0x3261 | SimC | SIM the roof is closing | RW | 16993 | 0
%MX1218.1 | Qopening_SIM | SIM_Variables | BOOL | FALSE | 0x3261 | SimO | SIM the roof is opening | RW | 16993 | 1
SensorsRoofPosition
%M1220.0 | sensor_closed_1A_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSC1A | Sim status closed side 1 A | RW | 16994 | 0
%M1220.1 | sensor_closed_1B_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSC1B | Sim status closed side 1 B | RW | 16994 | 1
%M1220.2 | sensor_open_1A_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSO1A | Sim status open side 1 A | RW | 16994 | 2
%M1220.3 | sensor_open_1B_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSO1B | Sim status open side 1 B | RW | 16994 | 3
%M1220.4 | sensor_closed_2A_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSC2A | Sim status closed side 2 A | RW | 16994 | 4
%M1220.5 | sensor_closed_2B_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSC2B | Sim status closed side 2 B | RW | 16994 | 5
%M1220.6 | sensor_open_2A_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSO2A | Sim status open side 2 A | RW | 16994 | 6
%M1220.7 | sensor_open_2B_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSO2B | Sim status open side 2 B | RW | 16994 | 7
%M1221.0 | sensor_closed_1A_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEC1A | Sim error closed side 1 A | RW | 16994 | 8
%M1221.1 | sensor_closed_1B_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEC1B | Sim error closed side 1 B | RW | 16994 | 9
%M1221.2 | sensor_open_1A_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEO1A | Sim error open side 1 A | RW | 16994 | 10
%M1221.3 | sensor_open_1B_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEO1B | Sim error open side 1 B | RW | 16994 | 11
%M1221.4 | sensor_closed_2A_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEC2A | Sim error closed side 2 A | RW | 16994 | 12
%M1221.5 | sensor_closed_2B_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEC2B | Sim error closed side 2 B | RW | 16994 | 13
%M1221.6 | sensor_open_2A_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEO2A | Sim error open side 2 A | RW | 16994 | 14
%M1221.7 | sensor_open_2B_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEO2B | Sim error open side 2 B | RW | 16994 | 15
Monitoring
%M1224.0 | so_SIM | SIM_Variables | BOOL | x | 0x3264 | SimSO | Sim stop open | RW | 16996 | 0
%M1224.1 | sc_SIM | SIM_Variables | BOOL | x | 0x3264 | SimSC | Sim stop close | RW | 16996 | 1
%M1224.2 | auto_SIM | SIM_Variables | BOOL | x | 0x3264 | SimAUTO | Sim auto | RW | 16996 | 2
%M1224.3 | man_SIM | SIM_Variables | BOOL | x | 0x3264 | SimMAN | Sim manuel | RW | 16996 | 3
%M1224.4 | rol1_SIM | SIM_Variables | BOOL | x | 0x3264 | SimROL1 | Sim roof open lamp 1 | RW | 16996 | 4
%M1224.5 | rol2_SIM | SIM_Variables | BOOL | x | 0x3264 | SimROL2 | Sim roof open lamp 2 | RW | 16996 | 5
%M1224.6 | rcl1_SIM | SIM_Variables | BOOL | x | 0x3264 | SimRCL1 | Sim roof close lamp 1 | RW | 16996 | 6
%M1224.7 | rcl2_SIM | SIM_Variables | BOOL | x | 0x3264 | SimRCL2 | Sim roof close lamp 2 | RW | 16996 | 7
%M1225.0 | mr_SIM | SIM_Variables | BOOL | x | 0x3264 | SimMR | Sim main motor | RW | 16996 | 8
%M1225.1 | nmr_SIM | SIM_Variables | BOOL | x | 0x3264 | SimNMR | Sim not main motor | RW | 16996 | 9
%M1225.2 | srs_SIM | SIM_Variables | BOOL | x | 0x3264 | SimSRS | Sim Safety Relay Stop | RW | 16996 | 10
%M1230 | d12v_SIM | SIM_Variables | UINT | x | 0x3267 | Sim12V |  | RW | 16999
Alarms
%M1232.0 | alarm_out_SIM | SIM_Variables | BOOL | x | 0x3268 | SimAlOut | Alarm roof position | RO | 17000 | 0
%M1232.1 | alarm_weather_SIM | SIM_Variables | BOOL | x | 0x3268 | SimAlWth | Alarm weather station | RO | 17000 | 1
Internal Variable (without allocation)
PLC
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init
% | IS_OCS_CONNECTED | Global_Variables | BOOL | TRUE
%11 | RESTORE_REGISTER | Global_Variables | BOOL | TRUE
%12
%13 | ValMax (set by Dylos_Big_ValMax) | DYLOS_DUSTED | INT | none
%14 | DylosParticlesValue | DYLOS_DUSTED | WORD | none
%15 | DylosDusty | DYLOS_DUSTED | BOOL | FALSE
%16
%17 | CMD_BUFF | Registers_Buff (RETAIN) | BOOL | none
%19 | EN_MDUST_SENSOR_BUFF | Registers_Buff (RETAIN) | BOOL | TRUE
%20 | EN_RAIN_BUFF | Registers_Buff (RETAIN) | BOOL | TRUE
%21 | EN_DYLOS_DUST_SENSOR_BUFF | Registers_Buff (RETAIN) | BOOL | TRUE
%22 | EN_CONTROL_WEATHER_STATION_BUFF | Registers_Buff (RETAIN) | BOOL | TRUE
%23 | EN_SIDE1_isOPEN_A_BUFF | Registers_Buff (RETAIN) | BOOL | FALSE
%24 | EN_SIDE1_isOPEN_B_BUFF | Registers_Buff (RETAIN) | BOOL | FALSE
%25 | EN_SIDE1_isCLOSED_A_BUFF | Registers_Buff (RETAIN) | BOOL | FALSE
%26 | EN_SIDE1_isCLOSED_B_BUFF | Registers_Buff (RETAIN) | BOOL | FALSE
%27 | EN_SIDE2_isOPEN_A_BUFF | Registers_Buff (RETAIN) | BOOL | FALSE
%28 | EN_SIDE2_isOPEN_B_BUFF | Registers_Buff (RETAIN) | BOOL | FALSE
%29 | EN_SIDE2_isCLOSED_A_BUFF | Registers_Buff (RETAIN) | BOOL | FALSE
%30 | EN_SIDE2_isCLOSED_B_BUFF | Registers_Buff (RETAIN) | BOOL | FALSE
%31 | EN_CTR_BUFF | Registers_Buff (RETAIN) | BOOL | FALSE
%32 | MDust_ValMax_BUFF | Registers_Buff (RETAIN) | UINT | 4000
%33 | MDust_ValMin_BUFF | Registers_Buff (RETAIN) | UINT | 2000
%34 | CTR_BUFF | Registers_Buff (RETAIN) | UINT | none
%35 | CTR_COPY | Registers_Buff (RETAIN) | UINT | none
%36 | CT_BUFF | Registers_Buff (RETAIN) | UINT | 10000
%37 | OCT_BUFF | Registers_Buff (RETAIN) | UINT | 60000
%38 | RELAY_RAIN_1_BUFF | Registers_Buff (RETAIN) | BOOL | TRUE
%39 | RELAY_RAIN_2_BUFF | Registers_Buff (RETAIN) | BOOL | TRUE
%40 | TClose_BUFF | Registers_Buff (RETAIN) | INT | none
%41 | TOpen_BUFF | Registers_Buff (RETAIN) | INT | none