## Beckhoff_IO_dispatch
|  | Box 1 |  | Term 2 |  |  |  | Term 3 |  | Term 4 |  |  |  | NC |  | Term 6 |  | Term 7 |  | Term 8 |  | Term 9 |  | Term 10 |  | Term 11 |  | Term 12 |  | NC |  | Term 14 |  | Term 15 |  | Borne Finale
Ethernet TCP/IP |  | X0 | 00 | 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34
| LED : TC/DC | Power LED 1 | Power LED 2 | Signal LED 1 | Signal LED 2 |  |  | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 |  |  | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | LED Run
| LED : ACT | Term 2 01: Signal LED 3; Term 2 02: Signal LED 4; Term 3 05: Signal LED 3; Term 3 06: Signal LED 4; Term 4 07: Signal LED 3; Term 4 08: Signal LED 4; NC 11: Signal LED 3; NC 12: Signal LED 4; Term 6 13: Error LED 1; Term 6 14: Error LED 2; Term 7 15: Error LED 1; Term 7 16: Error LED 2; Term 8 17: Error LED 1; Term 8 18: Error LED 2; Term 9 19: Error LED 1; Term 9 20: Error LED 2; Term 14 29: Signal LED 3; Term 14 30: Signal LED 4; Term 15 31: LED TxD; Term 15 32: LED RxD
| LED : ERROR | Term 2 01: Signal LED 5; Term 2 02: Signal LED 6; Term 3 05: Signal LED 5; Term 3 06: Signal LED 6; Term 4 07: Signal LED 5; Term 4 08: Signal LED 6; NC 11: Signal LED 5; NC 12: Signal LED 6
| LED : PLC | Term 2 01: Signal LED 7; Term 2 02: Signal LED 8; Term 3 05: Signal LED 7; Term 3 06: Signal LED 8; Term 4 07: Signal LED 7; Term 4 08: Signal LED 8; NC 11: Signal LED 7; NC 12: Signal LED 8
| LED : I/O RUN | 24V | 0V | Input 1 | Input 2 | 24V | 24V | Input 1 | Input 2 | Input 1 | Input 2 | 24V | 24V | Input 1 | Input 2 | +Input1 | +Input2 | +Input1 | +Input2 | +Input1 | +Input2 | +Input1 | +Input2 | Contact 1 | Contact 2 | Contact 1 | Contact 2 | Contact 1 | Contact 2 | Contact 1 | Contact 2 | +Input1 | +Input2 | TxD | RxD
Ethernet RJ45 Connector | LED : I/O ERR | Terminal POWER +24VDC | Terminal POWER GND | Daylight Sensor | Rain Sensor | Daylight 24V / Rain / 24V | Quittance #1 24V | Quittance STOP OPEN | Quittance Stop CLOSE | Quittance MR | Quittancenot MR | Quittance #2 24V |  | NC | NC | NAMUR BK Connector closed side 1 A | NAMUR BK Connector closed side 1 B | NAMUR BK Connector open side 1 A | NAMUR BK Connector open side 1 B | NAMUR BK Connector closed side 2 A | NAMUR BK Connector closed side 2 B | NAMUR BK Connector open side 2 A | NAMUR BK Connector open side 2 B | Command RCC OUT | Command ROC OUT | Command Telescope Camera 1-6 OUT | Command Telescope Camera 7-12 OUT | Command Alarm Roof OUT | Command Clim #1 OUT (Reserve) | Command Clim #2 OUT (Reserve) | NC | M-Dust PM | NC | Dust sensor Transmit Data | Dust Sensor Receive Data
|  | 1 | 5 | 1 | 5 | 1/2 | 9/10 | 1 | 5 | 1 | 5 | 1/2 | 9/10 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5
|  | + | + | Input 3 | Input 4 | 24V | 24V | Input 3 | Input 4 | Input 3 | Input 4 | 24V | 24V | Input 3 | Input 4 | 24V | 24V | 24V | 24V | 24V | 24V | 24V | 24V | Contact 1 | Contact 2 | Contact 1 | Contact 2 | Contact 1 | Contact 2 | Contact 1 | Contact 2 | +Input 3 | +Input 4 | RTS | CTS
|  | Terminal POWER +24VDC |  | Quittance Breaker1 | Quittance Breaker2 | Breaker1 24V / 24V / Breaker2 |  | Quittance AUTO | Quittance MAN | Quittance Safety relay | Quittance Roof Motor + Battery | QRMB 24V |  | NC | NC | [8 empty] | Command RCC IN | Command ROC IN | Command Telescope Camera 1-6 IN | Command Telescope Camera 7-12 IN | Command Alarm Roof IN | Command Clim #1 IN (Reserve) | Command Clim #2 IN (Reserve) | NC | NC | NC | Dust sensor Request to send | Dust sensor Clear to send
|  | 2 | 6 | 2 | 6 | 3/4 | 11/12 | 2 | 6 | 2 | 6 | 3/4 | 11/12 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6
Address Selector |  | - | - | Input 5 | Input 6 | 24V | 24V | Input 5 | Input 6 | Input 5 | Input 6 | 24V | 24V | Input 5 | Input 6 | 0V | 0V | 0V | 0V | 0V | 0V | 0V | 0V | NC | NC | NC | NC | NC | NC | NC | NC | GND | GND | M | M
|  | Terminal POWER GND |  | Quittance Breaker3 | Quittance UPS1 | Breaker3 24V / 24V / UPS1 |  | Quittance ROL1 | Quittance ROL2 | Quittance Telescope Camera 1-6 | Quittance Telescope Camera 7-12 | QTC1-6 24V / 24V / QTC7-12 |  | NC | NC | [16 empty] | M-DUST GND | NC | Dust sensor System ground | NC
|  | 3 | 7 | 3 | 7 | 5/6 | 13/14 | 3 | 7 | 3 | 7 | 5/6 | 13/14 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7
|  | PE | PE | Input 7 | Input 8 | 24V | 24V | Input 7 | Input 8 | Input 7 | Input 8 | 24V | 24V | Input 7 | Input 8 | -Input1 | -Input2 | -Input1 | -Input2 | -Input1 | -Input2 | -Input1 | -Input2 | PE | PE | PE | PE | PE | PE | PE | PE | PE | PE | S | S
| Configuration and programming Interface | CRATE IN Metalic DIN Profil | 21/4 | Quittance UPS2 | Quittance UPS3 (Reserve) | UPS2 24V / 24V / UPS3 |  | Quittance RCL1 | Quittance RCL2 | Quittance Clim #1 (Reserve) | Quittance Clim #2 (Reserve) | QC1 24V / 24V / QC2 |  | NC | NC | NAMUR BU Connector closed side 1 A | NAMUR BU Connector closed side 1 B | NAMUR BU Connector open side 1 A | NAMUR BU Connector open side 1 B | NAMUR BU Connector closed side 2 A | NAMUR BU Connector closed side 2 B | NAMUR BU Connector open side 2 A | NAMUR BU Connector open side 2 B | 00/8 | [9 empty] | NC | NC
|  | 4 | 8 | 4 | 8 | 7/8 | 15/16 | 4 | 8 | 4 | 8 | 7/8 | 15/16 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8
BC9020 |  | Term 2 01: KL1408; Term 2 03: KL9188; Term 3 05: KL1408; Term 4 07: KL1408; Term 4 09: KL9188; NC 11: KL1408; Term 6 13: KL1352; Term 7 15: KL1352; Term 8 17: KL1352; Term 9 19: KL1352; Term 10 21: KL2622; Term 11 23: KL2622; Term 12 25: KL2622; NC 27: KL2622; Term 14 29: KL3064; Term 15 31: KL6031; Borne Finale 33: KL9010
Beckhoff |  | Term 2 01: Beckhoff; Term 2 03: Beckhoff; Term 3 05: Beckhoff; Term 4 07: Beckhoff; Term 4 09: Beckhoff; NC 11: Beckhoff; Term 6 13: Beckhoff; Term 7 15: Beckhoff; Term 8 17: Beckhoff; Term 9 19: Beckhoff; Term 10 21: Beckhoff; Term 11 23: Beckhoff; Term 12 25: Beckhoff; NC 27: Beckhoff; Term 14 29: Beckhoff; Term 15 31: Beckhoff; Borne Finale 33: Beckhoff
Ethernet TCP/IP "Economy plus"Bus Terminal Controllers |  | Term 2 01: 8 channel digital input terminal 24V DC; Term 2 03: Potential distribution terminals 16x 24V; Term 3 05: 8 channel digital input terminal 24V DC; Term 4 07: 8 channel digital input terminal 24V DC; Term 4 09: Potential distribution terminals 16x 24V; NC 11: 8 channel digital input terminal 24V DC; Term 6 13: 2-channel digital input terminal 24V DC for NAMUR sensor; Term 7 15: 2-channel digital input terminal 24V DC for NAMUR sensor; Term 8 17: 2-channel digital input terminal 24V DC for NAMUR sensor; Term 9 19: 2-channel digital input terminal 24V DC for NAMUR sensor; Term 10 21: 2-channel relay output terminal 230V AC Inductive 2A Ohmiq 5A; Term 11 23: 2-channel relay output terminal 230V AC Inductive 2A Ohmiq 5A; Term 12 25: 2-channel relay output terminal 230V AC Inductive 2A Ohmiq 5A; NC 27: 2-channel relay output terminal 230V AC Inductive 2A Ohmiq 5A; Term 14 29: 4-channel analog input terminal 0…10V - 12bits resolution; Term 15 31: Serial Interface Terminal RS232; Borne Finale 33: Terminal bus extension, end terminal
| Power Contact | Box 1 X0: Power Contact Bus +24VDC
| Power Contact | Box 1 X0: Power Contact Bus 0V
Power Contact | bar: Box 1 X0 to Box 1 00; Term 10 21 to Term 15 32
[24 empty] | Contact sec | Contact sec | Contact sec | Contact sec | Contact sec | Contact sec | Contact sec | Contact sec

## Beckhoff_IO_dispatch (2)
Ethernet TCP/IP |  | X0 | 00 | 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34
| LED : TC/DC | Power LED 1 | Power LED 2 | Signal LED 1 | Signal LED 2 |  |  | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 |  |  | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | Signal LED 1 | Signal LED 2 | LED Run
| LED : ACT | 01: Signal LED 3; 02: Signal LED 4; 05: Signal LED 3; 06: Signal LED 4; 07: Signal LED 3; 08: Signal LED 4; 11: Signal LED 3; 12: Signal LED 4; 13: Error LED 1; 14: Error LED 2; 15: Error LED 1; 16: Error LED 2; 17: Error LED 1; 18: Error LED 2; 19: Error LED 1; 20: Error LED 2; 29: Signal LED 3; 30: Signal LED 4; 31: LED TxD; 32: LED RxD
| LED : ERROR | 01: Signal LED 5; 02: Signal LED 6; 05: Signal LED 5; 06: Signal LED 6; 07: Signal LED 5; 08: Signal LED 6; 11: Signal LED 5; 12: Signal LED 6
| LED : PLC | 01: Signal LED 7; 02: Signal LED 8; 05: Signal LED 7; 06: Signal LED 8; 07: Signal LED 7; 08: Signal LED 8; 11: Signal LED 7; 12: Signal LED 8
| LED : I/O RUN | 24V | 0V | Input 1 | Input 2 | 24V | 24V | Input 1 | Input 2 | Input 1 | Input 2 | 24V | 24V | Input 1 | Input 2 | +Input1 | +Input2 | +Input1 | +Input2 | +Input1 | +Input2 | +Input1 | +Input2 | Contact 1 | Contact 2 | Contact 1 | Contact 2 | Contact 1 | Contact 2 | Contact 1 | Contact 2 | +Input1 | +Input2 | TxD | RxD
Ethernet RJ45 Connector | LED : I/O ERR | Terminal POWER +24VDC | Terminal POWER GND | QDLS | QRS | QDLS-24 / / / QRS-24 | Q1-RCC-24 | QSO-RCC | QSC-RCC | QMR-RCC | QNMR-RCC | Q2-RCC-24 |  | NC | NC | NA-BK-C1A | NA-BK-C1B | NA-BK-O1A | NA-BK-O1B | NA-BK-C2A | NA-BK-C2B | NA-BK-O2A | NA-BK-O2B | CRCC2-RCC | CROC2-RCC | CTC1-6 | CTC7-12 | CALR1 | CC1-2 (Reserve) | CC2-2 (Reserve) | NC | M-Dust PM | NC | TxD | RxD
|  | 1 | 5 | 1 | 5 | 1/2 | 9/10 | 1 | 5 | 1 | 5 | 1/2 | 9/10 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5 | 1 | 5
|  | + | + | Input 3 | Input 4 | 24V | 24V | Input 3 | Input 4 | Input 3 | Input 4 | 24V | 24V | Input 3 | Input 4 | 24V | 24V | 24V | 24V | 24V | 24V | 24V | 24V | Contact 1 | Contact 2 | Contact 1 | Contact 2 | Contact 1 | Contact 2 | Contact 1 | Contact 2 | +Input 3 | +Input 4 | RTS | CTS
|  | Terminal POWER +24VDC |  | QBPASU1 | QBPASU2 | QBPASU1-24 / QBPASU2-24 |  | QAUTO-RCC | QMAN-RCC | QSRS-RCC | QRMB-RCC | QRMB-RCC-24 |  | NC | NC | [8 empty] | CRCC1-RCC | CROC1-RCC | CTC1-6-24 | CTC7-12-24 | CALR2 | CC1-1 (Reserve) | CC2-1 (Reserve) | NC | NC | NC | RTS | CTS
|  | 2 | 6 | 2 | 6 | 3/4 | 11/12 | 2 | 6 | 2 | 6 | 3/4 | 11/12 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6 | 2 | 6
Address Selector |  | - | - | Input 5 | Input 6 | 24V | 24V | Input 5 | Input 6 | Input 5 | Input 6 | 24V | 24V | Input 5 | Input 6 | 0V | 0V | 0V | 0V | 0V | 0V | 0V | 0V | NC | NC | NC | NC | NC | NC | NC | NC | GND | GND | M | M
|  | Terminal POWER GND |  | QBMB1 | QUPS1 | QBMB1-24 / / QUPS1-24 |  | QROL1-RCC | QROL2-RCC | QTC1-6 | QTC7-12 | QTC1-6-24 / / QTC7-12-24 |  | NC | NC | [16 empty] | M-DUST GND | NC | NC | NC
|  | 3 | 7 | 3 | 7 | 5/6 | 13/14 | 3 | 7 | 3 | 7 | 5/6 | 13/14 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7 | 3 | 7
|  | PE | PE | Input 7 | Input 8 | 24V | 24V | Input 7 | Input 8 | Input 7 | Input 8 | 24V | 24V | Input 7 | Input 8 | -Input1 | -Input2 | -Input1 | -Input2 | -Input1 | -Input2 | -Input1 | -Input2 | PE | PE | PE | PE | PE | PE | PE | PE | PE | PE | S | S
| Configuration and programming Interface | CRATE IN Metalic DIN Profil | 21/4 | QUPS2 | QUPS3 (Reserve) | QUPS2-24 / / /QUP3-24 |  | QRCL1-RCC | QRCL2-RCC | QC1 (Reserve) | QC2 (Reserve) | QC1- 24 / / QC2-24 |  | NC | NC | NA-BU-C1A | NA-BU-C1B | NA-BU-O1A | NA-BU-O1B | NA-BU-C2A | NA-BU-C2B | NA-BU-O2A | NA-BU-O2B | 00/8 | [9 empty] | NC | NC
|  | 4 | 8 | 4 | 8 | 7/8 | 15/16 | 4 | 8 | 4 | 8 | 7/8 | 15/16 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8 | 4 | 8
BC9020 |  | 01: KL1408; 03: KL9188; 05: KL1408; 07: KL1408; 09: KL9188; 11: KL1408; 13: KL1352; 15: KL1352; 17: KL1352; 19: KL1352; 21: KL2622; 23: KL2622; 25: KL2622; 27: KL2622; 29: KL3064; 31: KL6031; 33: KL9010
Beckhoff |  | 01: Beckhoff; 03: Beckhoff; 05: Beckhoff; 07: Beckhoff; 09: Beckhoff; 11: Beckhoff; 13: Beckhoff; 15: Beckhoff; 17: Beckhoff; 19: Beckhoff; 21: Beckhoff; 23: Beckhoff; 25: Beckhoff; 27: Beckhoff; 29: Beckhoff; 31: Beckhoff; 33: Beckhoff
Ethernet TCP/IP "Economy plus"Bus Terminal Controllers |  | 01: 8 channel digital input terminal 24V DC; 03: Potential distribution terminals 16x 24V; 05: 8 channel digital input terminal 24V DC; 07: 8 channel digital input terminal 24V DC; 09: Potential distribution terminals 16x 24V; 11: 8 channel digital input terminal 24V DC; 13: 2-channel digital input terminal 24V DC for NAMUR sensor; 15: 2-channel digital input terminal 24V DC for NAMUR sensor; 17: 2-channel digital input terminal 24V DC for NAMUR sensor; 19: 2-channel digital input terminal 24V DC for NAMUR sensor; 21: 2-channel relay output terminal 230V AC Inductive 2A Ohmiq 5A; 23: 2-channel relay output terminal 230V AC Inductive 2A Ohmiq 5A; 25: 2-channel relay output terminal 230V AC Inductive 2A Ohmiq 5A; 27: 2-channel relay output terminal 230V AC Inductive 2A Ohmiq 5A; 29: 4-channel analog input terminal 0…10V - 12bits resolution; 31: Serial Interface Terminal RS232; 33: Terminal bus extension, end terminal
| Power Contact | X0: Power Contact Bus +24VDC
| Power Contact | X0: Power Contact Bus 0V
Power Contact | bar: X0 to 00; 21 to 32
[24 empty] | Contact sec | Contact sec | Contact sec | Contact sec | Contact sec | Contact sec | Contact sec | Contact sec

## Feuil1
HARDWARE | [5 empty] | SOFTWARE |  |  |  | Drawing
Cable Name | Description | Beckhoff Terminal Number (type) | Position | Range Nominal (Expected) | Linked with | Software I/O Name | Software I/O Mapping | Software Memory Name | Software Modbus Memory
QDLS | Quittance of the Daylight Sensor | KL1408 (8 channel digital input terminal) | 1/1 | 24V DC (0V or 24V) | QDLS-24 | sensor_daylight | %IX0.0 | mem_light_value | %MX4.1 (0x4002 bit1) | #2 DISTRIBUTION BOARD NGTS FACILITY
QDLS-24 | 24V DC for Daylight Sensor | KL9188 (Potential distribution terminals 16x 24V) | 3/1 | 24V DC | QDLS | x | x | x | x
QRS | Quittance of the Rain Sensor | KL1408 (8 channel digital input terminal) | 2/5 | 24V DC (0V or 24V) | QRS-24 | sensor_rain | %IX0.1 | mem_rain_value | %MX4.5 (0x4002 bit5)
QRS-24 | 24V DC for Rain Sensor | KL9188 (Potential distribution terminals 16x 24V) | 3/2 | 24V DC | QRS | x | x | x | x
QBPASU1 | Quittance Breaker Parasurtension 1 | KL1408 (8 channel digital input terminal) | 1/2 | 24V DC (0V or 24V) | QBPASU1-24 | sensor_breaker1 | %IX0.2 | mem_breaker1 | %MX12.6 (0x4006 bit6)
QBPASU1-24 | 24V DC for Quittance Breaker Parasurtension 1 | KL9188 (Potential distribution terminals 16x 24V) | 3/3 | 24V DC | QBPASU1 | x | x | x | x | #1 CONNEXION BOARD BUILDING NGTS
QBPASU2 | Quittance Breaker Parasurtension 2 | KL1408 (8 channel digital input terminal) | 2/6 | 24V DC (0V or 24V) | QBPASU2-24 | sensor_breaker2 | %IX0.3 | mem_breaker2 | %MX12.7 (0x4006 bit7)
QBPASU2-24 | 24V DC for Quittance Breaker Parasurtension 2 | KL9188 (Potential distribution terminals 16x 24V) | 3/4 | 24V DC | QBPASU2 | x | x | x | x | #2 DISTRIBUTION BOARD NGTS FACILITY
QBMB1 | Quittance Breaker Main Breaker 1 | KL1408 (8 channel digital input terminal) | 1/3 | 24V DC (0V or 24V) | QBMB1-24 | sensor_breaker3 | %IX0.4 | mem_breaker3 | %MX13.0 (0x4006 bit8)
QBMB1-24 | 24V DC for Quittance Breaker 3 | KL9188 (Potential distribution terminals 16x 24V) | 3/5 | 24V DC | QBMB1 | x | x | x | x
QUPS1 | Quittance UPS 1 | KL1408 (8 channel digital input terminal) | 2/7 | 24V DC (0V or 24V) | QUPS1-24 | sensor_UPS1 | %IX0.5 | mem_UPS1 | %MX13.1 (0x4006 bit9)
QUPS1-24 | 24V DC for Quittance UPS 1 | KL9188 (Potential distribution terminals 16x 24V) | 3/6 | 24V DC | QUPS1 | x | x | x | x
QUPS2 | Quittance UPS 2 | KL1408 (8 channel digital input terminal) | 1/4 | 24V DC (0V or 24V) | QUPS2-24 | sensor_UPS2 | %IX0.6 | mem_UPS2 | %MX13.2 (0x4006 bit10)
QUPS2-24 | 24V DC for Quittance UPS 2 | KL9188 (Potential distribution terminals 16x 24V) | 3/7 | 24V DC | QUPS2 | x | x | x | x
QUPS3 | Quittance UPS 3 (Reserve) | KL1408 (8 channel digital input terminal) | 2/8 | 24V DC (0V or 24V) | QUPS3-24 | x | x | x | x
QUPS3-24 | 24V DC for Quittance UPS 3 (Reserve) | KL9188 (Potential distribution terminals 16x 24V) | 3/8 | 24V DC | QUPS3 | x | x | x | x
QSO-RCC | Quittance STOP OPEN - Roof Control Circuit | KL1408 (8 channel digital input terminal) | 5/1 | 24V DC (0V or 24V) | Q1-RCC-24 & Q2-RCC-24 | so | %IX1.0 | so_mem | %MX20.0 (0x400A bit0) | #3 GRPRO ROOF CONTROL CIRCUITS
QSC-RCC | Quittance STOP CLOSE - Roof Control Circuit | KL1408 (8 channel digital input terminal) | 6/5 | 24V DC (0V or 24V) | - | sc | %IX1.1 | sc_mem | %MX20.1 (0x400A bit1)
QAUTO-RCC | Quittance Switch AUTO mode - Roof Control Circuit | KL1408 (8 channel digital input terminal) | 5/2 | 24V DC (0V or 24V) | - | auto | %IX1.2 | auto_mem | %MX20.2 (0x400A bit2)
QMAN-RCC | Quittance Switch MAN mode - Roof Control Circuit | KL1408 (8 channel digital input terminal) | 6/6 | 24V DC (0V or 24V) | - | man | %IX1.3 | man_mem | %MX20.3 (0x400A bit3)
QROL1-RCC | Quittance Roof open lamp side 1 - Roof Control Circuit | KL1408 (8 channel digital input terminal) | 5/3 | 24V DC (0V or 24V) | - | rol1 | %IX1.4 | rol1_mem | %MX20.4 (0x400A bit4)
Q1-RCC-24 | 24V DC #1 for Quittances from Roof Conctrol Circuit | KL9188 (Potential distribution terminals 16x 24V) | 4/9 | 24V DC | All Q*-RCC | x | x | x | x
QROL2-RCC | Quittance Roof open lamp side 2 - Roof Control Circuit | KL1408 (8 channel digital input terminal) | 6/7 | 24V DC (0V or 24V) | Q1-RCC-24 & Q2-RCC-24 | rol2 | %IX1.5 | rol2_mem | %MX20.5 (0x400A bit5)
QRCL1-RCC | Quittance Roof closed lamp side 1 - Roof Control Circuit | KL1408 (8 channel digital input terminal) | 5/4 | 24V DC (0V or 24V) | - | rcl1 | %IX1.6 | rcl1_mem | %MX20.6 (0x400A bit6)
QRCL2-RCC | Quittance Roof closed lamp side 2 - Roof Control Circuit | KL1408 (8 channel digital input terminal) | 6/8 | 24V DC (0V or 24V) | - | rcl2 | %IX1.7 | rcl2_mem | %MX20.7 (0x400A bit7)
QMR-RCC | Quittance MR - Roof Control Circuit | KL1408 (8 channel digital input terminal) | 7/1 | 24V DC (0V or 24V) | - | mr | %IX2.0 | mr_mem | %MX21.0 (0x400A bit8)
QNMR-RCC | Quittance not MR - Roof Control Circuit | KL1408 (8 channel digital input terminal) | 8/5 | 24V DC (0V or 24V) | - | nmr | %IX2.1 | nmr_mem | %MX21.1 (0x400A bit9)
QSRS-RCC | Quittance Safety Relay STOP- Roof Control Circuit | KL1408 (8 channel digital input terminal) | 7/2 | 24V DC (0V or 24V) | - | srs | %IX2.2 | srs_mem | %MX21.2 (0x400A bit10)
Q2-RCC-24 | 24V DC #2 for Quittances from Roof Conctrol Circuit | KL9188 (Potential distribution terminals 16x 24V) | 9/1 | 24V DC | All Q*-RCC | x | x | x | x | #2 DISTRIBUTION BOARD NGTS FACILITY
QRMB | Quittance Roof Motor + Battery | KL1408 (8 channel digital input terminal) | 8/6 | 24V DC (0V or 24V) | QRMB-24 | ? | ? | ? | ?
QRMB-24 | 24V DC for Quittance Roof Motor + Battery | KL9188 (Potential distribution terminals 16x 24V) | 9/3 | 24V DC | QRMB | x | x | x | x
QTC1-6 | Quittance Telescope Camera 1-6 | KL1408 (8 channel digital input terminal) | 7/3 | 24V DC (0V or 24V) | QTC1-6-24 | ? | ? | ? | ?
QTC1-6-24 | 24V DC for Quittance Telescope Camera 1-6 | KL9188 (Potential distribution terminals 16x 24V) | 9/5 | 24V DC | QTC1-6 | x | x | x | x
QTC7-12 | Quittance Telescope Camera 7-12 | KL1408 (8 channel digital input terminal) | 8/7 | 24V DC (0V or 24V) | QTC7-12-24 | ? | ? | ? | ?
QTC7-12-24 | 24V DC for Quittance Telescope Camera 7-12 | KL9188 (Potential distribution terminals 16x 24V) | 9/6 | 24V DC | QTC7-12 | x | x | x | x
QC1 | Quittance Clim #1 (Reserve) | KL1408 (8 channel digital input terminal) | 7/4 | 24V DC (0V or 24V) | QC1-24 | x | x | x | x
QC1-24 | 24V DC for Quittance Clim #1 (Reserve) | KL9188 (Potential distribution terminals 16x 24V) | 9/7 | 24V DC | QC1 | x | x | x | x
QC2 | Quittance Clim #2 (Reserve) | KL1408 (8 channel digital input terminal) | 8/8 | 24V DC (0V or 24V) | QC2-24 | x | x | x | x
QC2-24 | 24V DC for Quittance Clim #2 (Reserve) | KL9188 (Potential distribution terminals 16x 24V) | 9/8 | 24V DC | QC2 | x | x | x | x
NA-BKC-C1A | NAMUR Black Connector roof closed side 1 A | KL1352 (2-channel digital input terminal for NAMUR sensor) | 13/1 | - | NA-BUC-C1A | POSITION_FAILURE.side_1.sensor_closed_A | %IX4.0 | POSITION_FAILURE.side_1.sensor_closed_A_mem | %MX2.0 (0x4001 bit0) | #4 BECKHOFF NAMUR + ALARM
NA-BUC-C1A | NAMUR Blue Connector roof closed side 1 A | - | 13/4 | - | NA-BKC-C1A
NA-BKC-C1B | NAMUR Black Connector roof closed side 1 B | - | 14/5 | - | NA-BUC-C1B | POSITION_FAILURE.side_1.sensor_closed_B | %IX4.2 | POSITION_FAILURE.side_1.sensor_closed_B_mem | %MX2.1 (0x4001 bit1)
NA-BUC-C1B | NAMUR Blue Connector roof closed side 1 B | - | 14/8 | - | NA-BKC-C1B
NA-BKC-O1A | NAMUR Black Connector roof open side 1 A | - | 15/1 | - | NA-BUC-O1A | POSITION_FAILURE.side_1.sensor_open_A | %IX4.4 | POSITION_FAILURE.side_1.sensor_open_A_mem | %MX2.2 (0x4001 bit2)
NA-BUC-O1A | NAMUR Blue Connector roof open side 1 A | - | 15/4 | - | NA-BKC-O1A
NA-BKC-O1B | NAMUR Black Connector roof open side 1 B | - | 16/5 | - | NA-BUC-O1B | POSITION_FAILURE.side_1.sensor_open_B | %IX4.6 | POSITION_FAILURE.side_1.sensor_open_B_mem | %MX2.3 (0x4001 bit3)
NA-BUC-O1B | NAMUR Blue Connector roof open side 1 B | - | 16/8 | - | NA-BKC-O1B
NA-BKC-C2A | NAMUR Black Connector roof closed side 2 A | - | 17/1 | - | NA-BUC-C2A | POSITION_FAILURE.side_2.sensor_closed_A | %IX5.0 | POSITION_FAILURE.side_2.sensor_closed_A_mem | %MX2.4 (0x4001 bit4)
NA-BUC-C2A | NAMUR Blue Connector roof closed side 2 A | - | 17/4 | - | NA-BKC-C2A
NA-BKC-C2B | NAMUR Black Connector roof closed side 2 B | - | 18/5 | - | NA-BUC-C2B | POSITION_FAILURE.side_2.sensor_closed_B | %IX4.2 | POSITION_FAILURE.side_2.sensor_closed_B_mem | %MX2.5 (0x4001 bit5)
NA-BUC-C2B | NAMUR Blue Connector roof closed side 2 B | - | 18/8 | - | NA-BKC-C2B
NA-BKC-O2A | NAMUR Black Connector roof open side 2 A | - | 19/1 | - | NA-BUC-O2A | POSITION_FAILURE.side_2.sensor_open_A | %IX4.2 | POSITION_FAILURE.side_2.sensor_open_A_mem | %MX2.6 (0x4001 bit6)
NA-BUC-O2A | NAMUR Blue Connector roof open side 2 A | - | 19/4 | - | NA-BKC-O2A
NA-BKC-O2B | NAMUR Black Connector roof open side 2 B | - | 20/5 | - | NA-BUC-O2B | POSITION_FAILURE.side_2.sensor_open_B | %IX4.2 | POSITION_FAILURE.side_2.sensor_open_B_mem | %MX2.7 (0x4001 bit7) | #4 BECKHOFF NAMUR + ALARM
NA-BUC-O2B | NAMUR Blue Connector roof open side 2 B | - | 20/8 | - | NA-BKC-O2B
CALR2 | Command Alarm Roof - 2 | KL2622 (2-channel relay output terminal ) | 25/1 | - | CALR1 | alarm_out | %QX2.0 | alarm | %MX14.0 (0x4007 bit0)
CALR1 | Command Alarm Roof - 1 | - | 25/2 | - | CALR2
CRCC2-RCC | Command Roof Close Control - Command | - | 21/1 | 230 V AC/ 30 V DC Inductive 2A Ohmiq 5A (24V DC) | CRCC1-RCC | close | %QX0.0 | CLOSE_MEM | %MX12.0 (0x4006 bit0) | #3 GRPRO ROOF CONTROL CIRCUITS
CRCC1-RCC | Command Roof Close Control - 24V of the roof | - | 21/2 |  | CRCC2-RCC
CROC2-RCC | Command Roof Open Control - Command | - | 22/5 | - | CROC1-RCC | open | %QX0.1 | OPEN_MEM | %MX12.1 (0x4006 bit1)
CROC1-RCC | Command Roof Open Control - 24V of the roof | - | 22/6 |  | CROC2-RCC
CTC1-6 | Command Telescope Camera 1-6 - Command | - | 23/1 | - | CTC1-6-24 | RELAY_RAIN_1 | %QX1.0 | RELAY_RAIN_1_MEM | %MX1038.0 (0x4207 bit0) | #2 DISTRIBUTION BOARD NGTS FACILITY
CTC1-6-24 | Command Telescope Camera 1-6 - 24V of the PLC | - | 23/2 |  | CTC1-6
CTC7-12 | Command Telescope Camera 7-12 - Command | - | 24/5 | - | CTC7-12-24 | RELAY_RAIN_2 | %QX1.1 | RELAY_RAIN_2_MEM | %MX1038.1 (0x4207 bit1)
CTC7-12-24 | Command Telescope Camera 7-12 - 24V of the PLC | - | 24/6 |  | CTC7-12
CC1-2 | Command Clim #1 - 2 (Reserve) | - | 26/5 | - | CC1-1 | x | x | x | x
CC1-1 | Command Clim #1 - 1 (Reserve) | - | 26/6 |  | CC1-2
CC2-2 | Command Clim #2 - 2 (Reserve) | - | 27/1 | - | CC2-1 | x | x | x | x
CC2-1 | Command Clim #2 - 1 (Reserve) | - | 27/1 |  | CC2-2
PMS-DU | Output of the M-Dust Particle Sensor (PM) | KL3064 (4-channel analog input terminal 0…10V - 12bits resolution) | 29/1 | 0…10V (0…4V) | PMS-DU-GND | sensor_dust | %IW6 | mem_dust_val | %MW6 (0x4003 all bits)
PMS-DU-GND | GND of the M-Dust Particle Sensor | - | 29/3 | 0V | PMS-DU | x | x | x | x