## CX8090_Building
PLC Resource: INPUT
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory Hex | Name | Description | Register | address | position
%IX0.0 | sensor_daylight | DAYLIGHT | BOOL | x
%IX0.1 | sensor_rain | RAIN | BOOL | x
%IX0.2 | sensor_breaker06PF16 | BREAKERS | BOOL | x
%IX0.3 |  | BREAKERS | BOOL | x
%IX0.4 |  | BREAKERS | BOOL | x
%IX0.5 | sensor_UPS1 | BREAKERS | BOOL | x
%IX0.6 | sensor_UPS2 | BREAKERS | BOOL | x
%IX1.0 | so | MONITORING | BOOL | x
%IX1.1 | sc | MONITORING | BOOL | x
%IX1.2 | auto | MONITORING | BOOL | x
%IX1.3 | man | MONITORING | BOOL | x
%IX1.4 | rol1 | MONITORING | BOOL | x
%IX1.5 | rol2 | MONITORING | BOOL | x
%IX1.6 | rcl1 | MONITORING | BOOL | x
%IX1.7 | rcl2 | MONITORING | BOOL | x
%IX2.0 | mr | MONITORING | BOOL | x
%IX2.1 | nmr | MONITORING | BOOL | x
%IX2.2 | srs | MONITORING | BOOL | x
%IX4.0 | sensor_closed_1A | POSITION_ROOF_1 | BOOL | x
%IX4.1 | sensor_closed_1B | POSITION_ROOF_1 | BOOL | x
%IX4.2 | sensor_open_1A | POSITION_ROOF_1 | BOOL | x
%IX4.3 | sensor_open_1B | POSITION_ROOF_1 | BOOL | x
%IX4.4 | sensor_closed_2A | POSITION_ROOF_1 | BOOL | x
%IX4.5 | sensor_closed_2B | POSITION_ROOF_1 | BOOL | x
%IX4.6 | sensor_open_2A | POSITION_ROOF_1 | BOOL | x
%IX4.7 | sensor_open_2B | POSITION_ROOF_1 | BOOL | x
%IX5.0 | sensor_closed_1A_err | POSITION_ROOF_2 | BOOL | x
%IX5.1 | sensor_closed_1B_err | POSITION_ROOF_2 | BOOL | x
%IX5.2 | sensor_open_1A_err | POSITION_ROOF_2 | BOOL | x
%IX5.3 | sensor_open_1B_err | POSITION_ROOF_2 | BOOL | x
%IX5.4 | sensor_closed_2B_err | POSITION_ROOF_2 | BOOL | x
%IX5.5 | sensor_closed_2A_err | POSITION_ROOF_2 | BOOL | x
%IX5.6 | sensor_open_2A_err | POSITION_ROOF_2 | BOOL | x
%IX5.7 | sensor_open_2B_err | POSITION_ROOF_2 | BOOL | x
%IW6 | MDust_Value | M_DUST | UINT | x
%IW8 | d12v |  | UINT | x
PLC Resource: OUTPUT
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory Hex | Name | Description | Register | address | position
%QX0.0 | Qclosing | Global_Variables | BOOL
%QX0.1 | Qopening | Global_Variables | BOOL
%QX1.0 | Qrelay_rain_1 | ReadWriteRegisters | BOOL
%QX1.1 | Qrelay_rain_2 | ReadWriteRegisters | BOOL
%QX2.0 | Qalarm_out | POSITION_FAILURE | BOOL
Resource: SoftwareVersioning
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory Hex | Name | Description | Register | address | position
%MB16 | Major | Soft versioning | USINT | x | 3008 | SoftwareVersioning1 |  | RO | 12296 | x
%MB17 | Minor | Soft versioning | USINT | x | 3008 | SoftwareVersioning1 |  | RO | 12296 | x
%MB18 | Development_stage | Soft versioning | USINT | x | 3009 | SoftwareVersioning2 |  | RO | 12297 | x
%MB19 | Revision_control | Soft versioning | USINT | x | 3009 | SoftwareVersioning2 |  | RO | 12297 | x
ReadWriteRegister
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory Hex | Name | Description | Register | address | position
Alarms
%MX14.0 | alarm_close | POSITION_FAILURE | BOOL | x | 3007 | AL | alarm | RO | 12295 | 0
%MX14.1 | error_1 | POSITION_FAILURE | BOOL | x | 3007 | ER1 | error side 1 | RO | 12295 | 1
%MX14.2 | error_2 | POSITION_FAILURE | BOOL | x | 3007 | ER2 | error side 2 | RO | 12295 | 2
%MX14.3 | blocked_1 | POSITION_FAILURE | BOOL | x | 3007 | BL1 | blocked side 1 | RO | 12295 | 3
%MX14.4 | blocked_2 | POSITION_FAILURE | BOOL | x | 3007 | BL2 | blocked side 2 | RO | 12295 | 4
%MX14.5 | alarm_weather | CONTROL_WEATHER_STATION | BOOL | x | 3007 | ALW | alarm weather | RO | 12295 | 5
%MX14.6 | pos_reached_1 |  |  |  | 3007 | PR1 | position reached 1 | RO | 12295 | 6
%MX14.7 | pos_reached_2 |  |  |  | 3007 | PR2 | position reached 2 | RO | 12295 | 7
%MX15.0 | pos_reached |  |  |  | 3007 | PR | position reached | RO | 12295 | 8
Commands
%MB1024 | CMD | ReadWriteRegisters | BYTE | x | 3200 | NONE (value="0") |  | RW | 12800 | x
%MB1024 | CMD | ReadWriteRegisters | BYTE | x | 3200 | CLOSE (value="1") |  | RW | 12800 | x
%MB1024 | CMD | ReadWriteRegisters | BYTE | x | 3200 | OPEN (value="2") |  | RW | 12800 | x
%MB1024 | CMD | ReadWriteRegisters | BYTE | x | 3200 | HIGH_OPEN (value="3") |  | RW | 12800 | x
EnableSensors1
[5 empty] | 3201 | ENABLE_ALL (value="65535") |  | RW | 12801 | x
[5 empty] | 3201 | DISABLE_ALL (value="0") |  | RW | 12801 | x
%MX1026.0 | EN_DAYLIGHT | ReadWriteRegisters | BOOL | x | 3201 | EnDL | enable daylight | RW | 12801 | 0
%MX1026.1 | EN_MDUST_SENSOR | ReadWriteRegisters | BOOL | x | 3201 | EnDU | enable M-dust sensor | RW | 12801 | 1
%MX1026.2 | EN_RAIN | ReadWriteRegisters | BOOL | x | 3201 | EnRN | enable rain | RW | 12801 | 2
%MX1026.3 | EN_SIDE1_isOPEN_A | ReadWriteRegisters | BOOL | x | 3201 | En1OA | enable side 1 open A | RW | 12801 | 3
%MX1026.4 | EN_SIDE1_isOPEN_B | ReadWriteRegisters | BOOL | x | 3201 | En1OB | enable side 1 open B | RW | 12801 | 4
%MX1026.5 | EN_SIDE1_isCLOSED_A | ReadWriteRegisters | BOOL | x | 3201 | EN1CA | enable side 1 closed A | RW | 12801 | 5
%MX1026.6 | EN_SIDE1_isCLOSED_B | ReadWriteRegisters | BOOL | x | 3201 | EN1CB | enable side 1 closed B | RW | 12801 | 6
%MX1026.7 | EN_SIDE2_isOPEN_A | ReadWriteRegisters | BOOL | x | 3201 | En2OA | enable side 2 open A | RW | 12801 | 7
%MX1027.0 | EN_SIDE2_isOPEN_B | ReadWriteRegisters | BOOL | x | 3201 | En2OB | enable side 2 open B | RW | 12801 | 8
%MX1027.1 | EN_SIDE2_isCLOSED_A | ReadWriteRegisters | BOOL | x | 3201 | EN2CA | enable side 2 closed A | RW | 12801 | 9
%MX1027.2 | EN_SIDE2_isCLOSED_B | ReadWriteRegisters | BOOL | x | 3201 | EN2CB | enable side 2 closed B | RW | 12801 | 10
%MX1027.3 | EN_CTR | ReadWriteRegisters | BOOL | x | 3201 | EnCTR | enable control | RW | 12801 | 11
%MX1027.4 | EN_DYLOS_DUST_SENSOR | ReadWriteRegisters | BOOL | x | 3201 | EnDU2 | enable Dylos dust sensor | RW | 12801 | 12
%MW1032 | CTR | ReadWriteRegisters | UINT | x | 3204 | Control |  | RW | 12804 | x
%MW1034 | CT | ReadWriteRegisters | UINT | x | 3205 | ControlTime |  | RW | 12805 | x
%MW1036 | OCT | ReadWriteRegisters | UINT | x | 3206 | OpeningClosingTime |  | RW | 12806 | x
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory Hex | Name | Description | Register | address | position
EnableSensors2
[5 empty] | 320A | ENABLE_ALL (value="65535") |  | RW | 12810 | x
[5 empty] | 320A | DISABLE_ALL (value="0") |  | RW | 12810 | x
%MX1044.0 | EN_sensor_breaker06PF16 | ReadWriteRegisters | BOOL |  | 320A | EnB1 | Enable breaker 1 | RW | 12810 | 0
%MX1044.1 |  | ReadWriteRegisters | BOOL |  | 320A | EnB2 | Enable breaker 2 | RW | 12810 | 1
%MX1044.2 |  | ReadWriteRegisters | BOOL |  | 320A | EnB3 | Enable breaker 3 | RW | 12810 | 2
%MX1044.3
%MX1044.4 | EN_sensor_UPS1 | ReadWriteRegisters | BOOL |  | 320A | EnU1 | Enable UPS 1 | RW | 12810 | 4
%MX1044.5 | EN_sensor_UPS2 | ReadWriteRegisters | BOOL |  | 320A | EnU2 | Enable UPS 2 | RW | 12810 | 5
RoofStatusBlocked
%MX1082.0 | ﻿blocked_leftInitialPosition_1 | MEM_Variables | BOOL |  | 321D | BLP1 | roof1 Not left initial pos | RO | 12829 | 0
%MX1082.1 | ﻿blocked_NotArrivedFinalPosition_1 | MEM_Variables | BOOL |  | 321D | BNAFP1 | roof1 Not arrived pos | RO | 12829 | 1
%MX1082.2 | ﻿blocked_leftInitialPosition_2 | MEM_Variables | BOOL |  | 321D | BLP2 | roof2 Not left initial pos | RO | 12829 | 2
%MX1082.3 | ﻿blocked_NotArrivedFinalPosition_2 | MEM_Variables | BOOL |  | 321D | BNAFP2 | roof2 Not arrived pos | RO | 12829 | 3
%MW1084 | NotLeftTime | ReadWriteRegisters | TIME | 10 | 321E | NotLeftTime |  | RW | 12830
%MW1088 | NotArrivedTime | ReadWriteRegisters | TIME | 100 | 3220 | NotArrivedTime |  | RW | 12832
%MB1092 | TOpen | ReadWriteRegisters | INT | 4 | 3222 | OpeningTemporisation |  | RW | 12834 | x
%MB1096 | TClose | ReadWriteRegisters | INT | 4 | 3224 | ClosingTemporisation |  | RW | 12836 | x
%MW1100 | TPowerOFF | ReadWriteRegisters | TIME | 30 | 3226 | Toff | Timer power OFF | RW | 12838
%MX1104.0 | ResetOff | ReadWriteRegisters | BOOL | False | 3228 | Rtoff | Reset T Power OFF | RW | 12840
MEM_Variables
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory Hex | Name | Description | Register | address | position
RoofPosition
%MX0.0 | isOpen_1_mem | MEM_Variables | BOOL | x | 3000 | O1 | is open side 1 | RO | 12288 | 0
%MX0.1 | isClosed_1_mem | MEM_Variables | BOOL | x | 3000 | C1 | is closed side 1 | RO | 12288 | 1
%MX0.2 | error_1_mem | MEM_Variables | BOOL | x | 3000 | E1 | error side 1 | RO | 12288 | 2
%MX0.3 | isOpen_2_mem | MEM_Variables | BOOL | x | 3000 | O2 | is open side 2 | RO | 12288 | 3
%MX0.4 | isClosed_2_mem | MEM_Variables | BOOL | x | 3000 | C2 | is closed side 2 | RO | 12288 | 4
%MX0.5 | error_2_mem | MEM_Variables | BOOL | x | 3000 | E2 | error side 2 | RO | 12288 | 5
SensorsRoofPosition
%MX2.0 | sensor_closed_1A_mem | MEM_Variables | BOOL | x | 3001 | SC1A | status closed side 1 A | RO | 12289 | 0
%MX2.1 | sensor_closed_1B_mem | MEM_Variables | BOOL | x | 3001 | SC1B | status closed side 1 B | RO | 12289 | 1
%MX2.2 | sensor_open_1A_mem | MEM_Variables | BOOL | x | 3001 | SO1A | status open side 1 A | RO | 12289 | 2
%MX2.3 | sensor_open_1B_mem | MEM_Variables | BOOL | x | 3001 | SO1B | status open side 1 B | RO | 12289 | 3
%MX2.4 | sensor_closed_2A_mem | MEM_Variables | BOOL | x | 3001 | SC2A | status closed side 2 A | RO | 12289 | 4
%MX2.5 | sensor_closed_2B_mem | MEM_Variables | BOOL | x | 3001 | SC2B | status closed side 2 B | RO | 12289 | 5
%MX2.6 | sensor_open_2A_mem | MEM_Variables | BOOL | x | 3001 | SO2A | status open side 2 A | RO | 12289 | 6
%MX2.7 | sensor_open_2B_mem | MEM_Variables | BOOL | x | 3001 | SO2B | status open side 2 B | RO | 12289 | 7
%MX3.0 | sensor_closed_1A_err_mem | MEM_Variables | BOOL | x | 3001 | EC1A | error closed side 1 A | RO | 12289 | 8
%MX3.1 | sensor_closed_1B_err_mem | MEM_Variables | BOOL | x | 3001 | EC1B | error closed side 1 B | RO | 12289 | 9
%MX3.2 | sensor_open_1A_err_mem | MEM_Variables | BOOL | x | 3001 | EO1A | error open side 1 A | RO | 12289 | 10
%MX3.3 | sensor_open_1B_err_mem | MEM_Variables | BOOL | x | 3001 | EO1B | error open side 1 B | RO | 12289 | 11
%MX3.4 | sensor_closed_2A_err_mem | MEM_Variables | BOOL | x | 3001 | EC2A | error closed side 2 A | RO | 12289 | 12
%MX3.5 | sensor_closed_2B_err_mem | MEM_Variables | BOOL | x | 3001 | EC2B | error closed side 2 B | RO | 12289 | 13
%MX3.6 | sensor_open_2A_err_mem | MEM_Variables | BOOL | x | 3001 | EO2A | error open side 2 A | RO | 12289 | 14
%MX3.7 | sensor_open_2B_err_mem | MEM_Variables | BOOL | x | 3001 | EO2B | error open side 2 B | RO | 12289 | 15
SensorStatus
%MX4.0 |  |  |  |  | 3002 |  |  |  | 12290 | 0
%MX4.1 | sensor_rain_mem | MEM_Variables | BOOL |  | 3002 | RNV | rain value | RO | 12290 | 1
%MX4.2 | sensor_daylight_mem | MEM_Variables | BOOL | x | 3002 | DLS | daylight status | RO | 12290 | 2
%MX4.3 |  |  |  |  | 3002 |  |  | RO | 12290 | 3
%MX4.4 |  |  |  |  | 3002 |  |  | RO | 12290 | 4
%MX4.5 |  |  |  |  | 3002 |  |  | RO | 12290 | 5
%MX4.6 |  |  |  |  | 3002 |  |  | RO | 12290 | 6
%MW6 | Mean_MDust_Value_mem | DUST | UINT | x | 3003 | mean DustValue |  | RO | 12291
%MW8 | MDust_Value_mem |  | UINT | x | 3004 | MDustValuemem |  | RO | 12292
%MX10.0 | Sensors_Detecting_mem | MEM_Variables | UINT | x | 3005 | SensorsDetecting |  | RO | 12293
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory Hex | Name | Description | Register | address | position
CmdRemoteCtrBreakers
%MX12.0 | opening_MEM | Commands | BOOL | x | 3006 | O | opening! | RO | 12294 | 0
%MX12.1 | CLOSE_MEM | Commands | BOOL | x | 3006 | C | closing! | RO | 12294 | 1
%MX12.2 | CMD_HAND | Commands | BOOL | x | 3006 | HAND | CMD_HAND | RO | 12294 | 2
%MX12.6 | sensor_breaker06PF16_mem | MEM_Variables | BOOL | x | 3006 | B1 | breaker 1 | RO | 12294 | 6
%MX12.7 |  | MEM_Variables | BOOL | x | 3006 |  |  | RO | 12294 | 7
%MX13.0 |  | MEM_Variables | BOOL | x | 3006 |  |  | RO | 12294 | 8
%MX13.1 | sensor_UPS1_mem | MEM_Variables | BOOL | x | 3006 | UPS1 | UPS1 4 | RO | 12294 | 9
%MX13.2 | sensor_UPS2_mem | MEM_Variables | BOOL | x | 3006 | UPS2 | UPS2 5 | RO | 12294 | 10
Monitoring
%MX20.0 | so_mem | MONITORING | BOOL |  | 300A | SO | STOP Open | RO | 12298 | 0
%MX20.1 | sc_mem | MONITORING | BOOL |  | 300A | SC | STOP Close | RO | 12298 | 1
%MX20.2 | auto_mem | MONITORING | BOOL |  | 300A | AUTO | Switch AUTO | RO | 12298 | 2
%MX20.3 | man_mem | MONITORING | BOOL |  | 300A | MAN | Switch MANUAL | RO | 12298 | 3
%MX20.4 | rol1_mem | MONITORING | BOOL |  | 300A | ROL1 | Roof Open Lamp 1 | RO | 12298 | 4
%MX20.5 | rol2_mem | MONITORING | BOOL |  | 300A | ROL2 | Roof Open Lamp 2 | RO | 12298 | 5
%MX20.6 | rcl1_mem | MONITORING | BOOL |  | 300A | RCL1 | Roof Close Lamp 1 | RO | 12298 | 6
%MX20.7 | rcl2_mem | MONITORING | BOOL |  | 300A | RCL2 | Roof Close Lamp 2 | RO | 12298 | 7
%MX21.0 | mr_mem | MONITORING | BOOL |  | 300A | MR | MR: Main Motor | RO | 12298 | 8
%MX21.1 | nmr_mem | MONITORING | BOOL |  | 300A | nMR | not MR: DC Motor Backup | RO | 12298 | 9
%MX21.2 | srs_mem | MONITORING | BOOL |  | 300A | SRS | Safety Relay STOP | RO | 12298 | 10
%MW22 | d12v_mem | MONITORING | UINT |  | 300B | Dust12VDC |  | RO | 12299 | x
ResetRelay
[5 empty] | 3207 | NONE (value="0") |  |  | 12807 | x
[5 empty] | 3207 | RESET_RELAY_1 (value="1") |  |  | 12807 | x
%MX1038.0 | Qrelay_rain_1_mem | ReadWriteRegisters | BOOL |  | 3207 | RESET_RELAY_2 (value="2") |  |  | 12807 | x
%MX1038.1 | Qrelay_rain_2_mem | ReadWriteRegisters | BOOL |  | 3207 | RESET_BOTH (value="3") |  |  | 12807 | x
[5 empty] | 3207 | R1 | Reset bit for relay 1 | RW | 12807 | 0
[5 empty] | 3207 | R2 | Reset bit for relay 2 | RW | 12807 | 1
%MW1064 | DylosBigParticles_mem | ReadWriteRegisters | WORD | x | 3214 | DylosBigValue |  | RW | 12820 | x
%MW1066 | DylosSmallParticles_mem | ReadWriteRegisters | WORD | x | 3215 | DylosSmallValue |  | RW | 12821 | x
%MX1080.0 | reset_mem | MEM_Variables | BOOL |  | 321C | ResBlocked | Reset Blocked state | RW | 12828 | 0
SIMULATION
PLC |  |  |  |  | plcconfig.html
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init | Memory Hex | Name | Description | Register | address | position
%MX1200.0 | SIMULATION | SIM_Variables | BOOL | FALSE | 0x3258 | SIMULATION |  | RW | 16984 | 0
%MX1202.0 | is_ocs_connected_SIM | SIM_Variables | BOOL | TRUE | 0x3259 | is_ocs_connected_SIM |  | RW | 16985 | 0
%MX1210.0 | MDust_Dusty_SIM | SIM_Variables | BOOL | FALSE | 0x325D | MDustValue_SIM |  | RW | 16989 | 0
%MX1212.0 | Dylos_Dusty_SIM | SIM_Variables | BOOL |  | 0x325E | DylosDusty_SIM |  | RW | 16990 | 0
%MW1214 |  |  |  |  | 0x325F |  |  | RW | 16991
SIM_sensor_state
%MX1216.0 | sensor_daylight_SIM | SIM_Variables | BOOL | TRUE | 0x3260 | SimDS | SIM state daylight sensor | RW | 16992 | 0
%MX1216.1 | sensor_rain_SIM | SIM_Variables | BOOL | x | 0x3260 | SimRS | SIM state rain sensor | RW | 16992 | 1
%MX1216.2 | sensor_breaker06PF16_SIM | SIM_Variables | BOOL | x | 0x3260 | SimB1 | SIM breaker1 state | RW | 16992 | 2
%MX1216.3 |  | SIM_Variables | BOOL | x | 0x3260 |  |  | RW | 16992 | 3
%MX1216.4 |  | SIM_Variables | BOOL | x | 0x3260 |  |  | RW | 16992 | 4
%MX1216.5 | sensor_UPS1_SIM | SIM_Variables | BOOL | x | 0x3260 | SimU1 | SIM UPS1 state | RW | 16992 | 5
%MX1216.6 | sensor_UPS2_SIM | SIM_Variables | BOOL | x | 0x3260 | SimU2 | SIM UPS2 state | RW | 16992 | 6
%MX1216.7 | Qrelay_rain_1_SIM | SIM_Variables | BOOL | x | 0x3260 | SimRR1 | SIM Rain1 | RW | 16992 | 7
%MX1217.0 | Qrelay_rain_2_SIM | SIM_Variables | BOOL | x | 0x3260 | SIMRR2 | SIM Rain2 | RW | 16992 | 8
SIM_Roof_State
%MX1218.0 | Qclosing_SIM | SIM_Variables | BOOL | FALSE | 0x3261 | SimC | SIM the roof is closing | RW | 16993 | 0
%MX1218.1 | Qopening_SIM | SIM_Variables | BOOL | FALSE | 0x3261 | SimO | SIM the roof is opening | RW | 16993 | 1
SensorsRoofPosition
%M1220.0 | sensor_closed_1A_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSC1A | Sim status closed side 1 A | RW | 16994 | 0
%M1220.1 | sensor_closed_1B_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSC1B | Sim status closed side 1 B | RW | 16994 | 1
%M1220.2 | sensor_open_1A_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSO1A | Sim status open side 1 A | RW | 16994 | 2
%M1220.3 | sensor_open_1B_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSO1B | Sim status open side 1 B | RW | 16994 | 3
%M1220.4 | sensor_closed_2A_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSC2A | Sim status closed side 2 A | RW | 16994 | 4
%M1220.5 | sensor_closed_2B_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSC2B | Sim status closed side 2 B | RW | 16994 | 5
%M1220.6 | sensor_open_2A_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSO2A | Sim status open side 2 A | RW | 16994 | 6
%M1220.7 | sensor_open_2B_SIM | SIM_Variables | BOOL | x | 0x3262 | SimSO2B | Sim status open side 2 B | RW | 16994 | 7
%M1221.0 | sensor_closed_1A_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEC1A | Sim error closed side 1 A | RW | 16994 | 8
%M1221.1 | sensor_closed_1B_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEC1B | Sim error closed side 1 B | RW | 16994 | 9
%M1221.2 | sensor_open_1A_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEO1A | Sim error open side 1 A | RW | 16994 | 10
%M1221.3 | sensor_open_1B_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEO1B | Sim error open side 1 B | RW | 16994 | 11
%M1221.4 | sensor_closed_2A_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEC2A | Sim error closed side 2 A | RW | 16994 | 12
%M1221.5 | sensor_closed_2B_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEC2B | Sim error closed side 2 B | RW | 16994 | 13
%M1221.6 | sensor_open_2A_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEO2A | Sim error open side 2 A | RW | 16994 | 14
%M1221.7 | sensor_open_2B_err_SIM | SIM_Variables | BOOL | x | 0x3262 | SimEO2B | Sim error open side 2 B | RW | 16994 | 15
Monitoring
%M1224.0 | so_SIM | SIM_Variables | BOOL | x | 0x3264 | SimSO | Sim stop open | RW | 16996 | 0
%M1224.1 | sc_SIM | SIM_Variables | BOOL | x | 0x3264 | SimSC | Sim stop close | RW | 16996 | 1
%M1224.2 | auto_SIM | SIM_Variables | BOOL | x | 0x3264 | SimAUTO | Sim auto | RW | 16996 | 2
%M1224.3 | man_SIM | SIM_Variables | BOOL | x | 0x3264 | SimMAN | Sim manuel | RW | 16996 | 3
%M1224.4 | rol1_SIM | SIM_Variables | BOOL | x | 0x3264 | SimROL1 | Sim roof open lamp 1 | RW | 16996 | 4
%M1224.5 | rol2_SIM | SIM_Variables | BOOL | x | 0x3264 | SimROL2 | Sim roof open lamp 2 | RW | 16996 | 5
%M1224.6 | rcl1_SIM | SIM_Variables | BOOL | x | 0x3264 | SimRCL1 | Sim roof close lamp 1 | RW | 16996 | 6
%M1224.7 | rcl2_SIM | SIM_Variables | BOOL | x | 0x3264 | SimRCL2 | Sim roof close lamp 2 | RW | 16996 | 7
%M1225.0 | mr_SIM | SIM_Variables | BOOL | x | 0x3264 | SimMR | Sim main motor | RW | 16996 | 8
%M1225.1 | nmr_SIM | SIM_Variables | BOOL | x | 0x3264 | SimNMR | Sim not main motor | RW | 16996 | 9
%M1225.2 | srs_SIM | SIM_Variables | BOOL | x | 0x3264 | SimSRS | Sim Safety Relay Stop | RW | 16996 | 10
%M1230 | d12v_SIM | SIM_Variables | UINT | x | 0x3267 | Sim12V |  | RW | 16999
Alarms
%M1232.0 | alarm_out_SIM | SIM_Variables | BOOL | x | 0x3268 | SimAlOut | Alarm roof position | RO | 17000 | 0
%M1232.1 | alarm_weather_SIM | SIM_Variables | BOOL | x | 0x3268 | SimAlWth | Alarm weather station | RO | 17000 | 1
Internal Variable (without allocation)
PLC
PLC Memory | PLC Name | PLC Resource | PLC type | PLC Init
% | IS_OCS_CONNECTED | Global_Variables | BOOL | TRUE
%11 | RESTORE_REGISTER | Global_Variables | BOOL | TRUE
%12
%14 | DylosParticlesValue | DYLOS_DUSTED | WORD | none
%15 | DylosDusty | DYLOS_DUSTED | BOOL | FALSE
%16